## Lines
| Substation 1 |  | Substation 2 |  |  | Maximum Current Imax (A) |  |  | Dynamic line rating (DLR) |  | Electrical Parameters
Circuit name | Full name | Short name | Full name | Short name | Voltage level (kV) | Summer | Interseason | Winter | DLRmin (A) | DLRmax (A) | Resistance R (W) | Reactance X (W) | Susceptance B (mS) | Length (km)
Altbach-Mühlhausen weiss | Altbach | AL1KW | Mühlhausen | MULHS | 400 | 2544 | - | 3000 | - | - | 0.8552 | 8.0173 | 140.2721 | 31.47
Altbach-Wendlingen blau | Altbach | AL1KW | Wendlingen | WDLNG | 400 | 2000 | - | 2000 | - | - | 0.1336 | 2.0393 | 31.8872 | 7.553
Altlußheim-Daxlanden blau | Altlußheim | ALHIM | Daxlanden | DAXLA | 225 | 2267 | - | 2267 | - | - | 1.1557 | 8.716 | 205.5228 | 38.03
Altlußheim-Großkraftwerk Mannheim blau | Altlußheim | ALHIM | Großkraftwerk Mannheim | WERKI | 225 | 2505 | - | 2651 | - | - | 0.6298 | 4.6745 | 127.4543 | 21.35
Beuren-Gurtweil gelb | Beuren | BRNKO | Gurtweil | GURTW | 225 | 2000 | - | 2000 | - | - | 2.321 | 18.534 | 385.4106 | 77.35
Beuren-Stockach blau | Beuren | BRNKO | Stockach | STOCK | 225 | 1980 | - | 1980 | - | - | 0.366 | 2.927 | 60.7898 | 12.2
Birkenfeld-Daxlanden gelb | Birkenfeld | BIRKN | Daxlanden | DAXLA | 225 | 1123 | - | 1283 | - | - | 0.9743 | 6.8269 | 141.2146 | 29.28
Bruchsal Kändelweg-Philippsburg-Pulverdingen rot BRUKA | Bruchsal Kändelweg | BRUKA | M043A-4 | M043A-4 | 400 | 598 | - | 598 | - | - | 0.1403 | 1.2425 | 24.6929 | 5.214
Bruchsal Kändelweg-Philippsburg-Pulverdingen rot PHILI | M043A-4 | M043A-4 | Philippsburg | PHILI | 400 | 2880 | - | 2880 | - | - | 0.3228 | 4.406 | 67.8584 | 16.3
Bruchsal Kändelweg-Philippsburg-Pulverdingen rot PULVE | Pulverdingen | PULVE | M043A-4 | M043A-4 | 400 | 2880 | - | 2880 | - | - | 1.0313 | 14.0056 | 216.4243 | 51.51
Bühl-Daxlanden-Kuppenheim rot BUEHL | Bühl | BUEHL | KUMRAY-2Y | KUMRAY-2Y | 225 | 1262 | - | 1595 | - | - | 1.2246 | 6.1931 | 82.027 | 21.142
Bühl-Daxlanden-Kuppenheim rot DAXLA | Daxlanden | DAXLA | KUMRAY-2Y | KUMRAY-2Y | 225 | 1262 | - | 1595 | - | - | 1.1643 | 5.7109 | 77.4717 | 19.844
Bühl-Daxlanden-Kuppenheim rot KUMRA | KUMRAY-2Y | KUMRAY-2Y | Kuppenheim | KUMRA | 225 | 855 | - | 855 | - | - | 0.0059 | 0.0319 | 0.40841 | 0.107
Bühl-Weier gruen | Bühl | BUEHL | Weier | WEIER | 225 | 1261 | - | 1595 | - | - | 1.6971 | 8.4966 | 111.5579 | 28.89
Bünzwangen-Laichingen gruen | Bünzwangen | BZWNG | Laichingen | LAICH | 400 | 2511 | - | 3000 | - | - | 1.0882 | 12.4149 | 192.1712 | 45.81
Bünzwangen-Wendlingen gelb | Bünzwangen | BZWNG | Wendlingen | WDLNG | 400 | 2080 | - | 2080 | - | - | 0.2279 | 3.3554 | 55.5434 | 12.81
Daxlanden-Eichstetten gruen | Daxlanden | DAXLA | Eichstetten | EICHS | 400 | 2352 | - | 2920 | - | - | 3.621 | 31.019 | 542.2389 | 120.7
Daxlanden-Eichstetten rot | Daxlanden | DAXLA | Eichstetten | EICHS | 400 | 2523 | - | 2850 | - | - | 3.62 | 30.41 | 547.2654 | 120.7
Daxlanden-Kuppenheim-Weier gelb DAXLA | KUMRAY-Y | KUMRAY-Y | Daxlanden | DAXLA | 225 | 2524 | - | 2565 | - | - | 0.5935 | 4.5624 | 98.1748 | 19.844
Daxlanden-Kuppenheim-Weier gelb KUMRA | KUMRAY-Y | KUMRAY-Y | Kuppenheim | KUMRA | 225 | 855 | - | 855 | - | - | 0.0059 | 0.0319 | 0.40841 | 0.107
Daxlanden-Kuppenheim-Weier gelb WEIER | KUMRAY-Y | KUMRAY-Y | Weier | WEIER | 225 | 2524 | - | 2567 | - | - | 1.4 | 10.7477 | 230.6871 | 46.705
Daxlanden-Neurott gelb | Daxlanden | DAXLA | Neurott | NEURO | 225 | 1253 | - | 1440 | - | - | 4.1793 | 19.5979 | 271.5907 | 66.44
Daxlanden-Oberwald rot | Daxlanden | DAXLA | Oberwald | OWALD | 225 | 1535 | - | 1916 | - | - | 0.4706 | 3.3368 | 63.0203 | 13.53
Daxlanden-Philippsburg gelb | Daxlanden | DAXLA | Philippsburg | PHILI | 400 | 3000 | - | 3000 | - | - | 0.588 | 8.737 | 138.6071 | 32.65
Daxlanden-Philippsburg rot | Daxlanden | DAXLA | Philippsburg | PHILI | 400 | 3000 | - | 3000 | - | - | 0.589 | 8.752 | 138.7641 | 32.7
Dellmensingen.Goldshöfe-Niederstotzingen GOHFE | Goldshöfe | GOHFE | 094_329-Y | 094_329-Y | 400 | 2565 | - | 3150 | - | - | 1.1996 | 12.3824 | 199.6168 | 46.74
Dellmensingen.Goldshöfe-Niederstotzingen weiss DELLM | Dellmensingen | DELLM | 094_329-Y | 094_329-Y | 400 | 1800 | - | 2404 | - | - | 1.0854 | 11.4919 | 164.2739 | 40.7
Dellmensingen.Goldshöfe-Niederstotzingen weiss NSTNG | Niederstotzingen | NSTNG | 094_329-Y | 094_329-Y | 400 | 556 | - | 556 | - | - | 0.0071 | 0.0613 | 0.81681 | 0.209
Dellmensingen-Hoheneck-Vöhringen rot DELLM | Dellmensingen | DELLM | 4104_212-Y | 4104_212-Y | 400 | 2720 | - | 2720 | - | - | 0.0083 | 0.0757 | 1.3509 | 0.3
Dellmensingen-Laichingen weiss | Laichingen | LAICH | Dellmensingen | DELLM | 400 | 2478 | - | 2880 | - | - | 0.6234 | 6.6472 | 101.0336 | 24.34
Dellmensingen-Rotensohl blau | Dellmensingen | DELLM | Rotensohl | ROLSO | 400 | 1800 | - | 2000 | - | - | 1.8914 | 18.5361 | 276.5858 | 67.15
Eichstetten-Gurtweil gelb | Eichstetten | EICHS | Gurtweil | GURTW | 225 | 1092 | - | 1200 | - | - | 4.654 | 22.715 | 256.8566 | 72.3
Eichstetten-Gurtweil rot | Eichstetten | EICHS | Gurtweil | GURTW | 225 | 1092 | - | 1200 | - | - | 4.654 | 22.715 | 256.8566 | 72.3
Eichstetten-Kühmoos gruen | Eichstetten | EICHS | Kühmoos | KUHMO | 400 | 2351 | - | 2351 | - | - | 2.501 | 21.423 | 374.4778 | 83.36
Eichstetten-Kühmoos rot | Eichstetten | EICHS | Kühmoos | KUHMO | 400 | 2508 | - | 2850 | - | - | 2.5 | 21.006 | 377.9336 | 83.31
Eichstetten-Weier gelb | Eichstetten | EICHS | Weier | WEIER | 225 | 2500 | - | 2500 | - | - | 1.4636 | 11.182 | 240.0177 | 48.78
Eichstetten-Weier rot | Eichstetten | EICHS | Weier | WEIER | 225 | 1261 | - | 1496 | - | - | 2.8785 | 14.3528 | 187.773 | 48.78
Endersbach-Großgartach-Mühlhausen gruen EDSBH | Endersbach | EDSBH | 326M10A-Y | 326M10A-Y | 400 | 2720 | - | 3000 | - | - | 0.4488 | 4.2618 | 75.0212 | 16.7
Endersbach-Großgartach-Mühlhausen gruen GROGH | Großgartach | GROGH | 326M10A-Y | 326M10A-Y | 400 | 2720 | - | 3160 | - | - | 0.5475 | 5.3337 | 170.777 | 27.11
Endersbach-Großgartach-Mühlhausen gruen MULHS | Mühlhausen | MULHS | 326M10A-Y | 326M10A-Y | 400 | 2720 | - | 3150 | - | - | 0.2368 | 2.4281 | 38.4217 | 8.937
Endersbach-Wendlingen blau | Endersbach | EDSBH | Wendlingen | WDLNG | 400 | 2080 | - | 2080 | - | - | 0.4998 | 5.2155 | 89.8495 | 20.307
Engstlatt-Kühmoos-Villingen gruen ENGST | Engstlatt | ENGST | M153-Y | M153-Y | 400 | 2880 | - | 2880 | - | - | 1.1125 | 14.7524 | 236.9703 | 55.37
Engstlatt-Kühmoos-Villingen gruen KUHMO | M153-Y | M153-Y | Kühmoos | KUHMO | 400 | 2578 | - | 3000 | - | - | 1.5359 | 17.7467 | 321.3535 | 68.04
Engstlatt-Kühmoos-Villingen gruen VILLI | M153-Y | M153-Y | Villingen | VILLI | 400 | 570 | - | 570 | - | - | 0.4531 | 3.816 | 78.2257 | 16.21
Engstlatt-Oberjettingen-Pulverdingen rot ENGST | Engstlatt | ENGST | M 1B-Y | M 1B-Y | 400 | 2487 | - | 2880 | - | - | 0.8572 | 9.016 | 145.5814 | 34.02
Engstlatt-Oberjettingen-Pulverdingen rot OBJTT | Oberjettingen | OBJTT | M 1B-Y | M 1B-Y | 400 | 3120 | - | 3120 | - | - | 0.0005 | 0.0053 | 0.094248 | 0.02
Engstlatt-Oberjettingen-Pulverdingen rot PULVE | Pulverdingen | PULVE | M 1B-Y | M 1B-Y | 400 | 2483 | - | 2880 | - | - | 1.166 | 12.1051 | 194.5902 | 45.58
Engstlatt-Trossingen rot | Engstlatt | ENGST | Trossingen | TRSNG | 400 | 2720 | - | 2880 | - | - | 0.7609 | 9.8951 | 159.7814 | 37.27
Goldshöfe-Kupferzell gruen | Goldshöfe | GOHFE | Kupferzell | KUPZL | 400 | 2656 | - | 3000 | - | - | 1.5275 | 13.8673 | 249.6624 | 55.25
Goldshöfe-Rotensohl gruen | Goldshöfe | GOHFE | Rotensohl | ROLSO | 400 | 2000 | - | 2000 | - | - | 0.5232 | 5.4399 | 86.5509 | 20.32
Großgartach-GKN schwarz | Großgartach | GROGH | GKN | GKN | 400 | 2621 | - | 3000 | - | - | 0.4718 | 4.3519 | 75.8066 | 16.93
Großgartach-Heilbronn rot | Großgartach | GROGH | Heilbronn | HLBRO | 400 | 2000 | - | 2000 | - | - | 0.207 | 1.9031 | 29.908 | 7.021
Großgartach-Hüffenhardt blau | Großgartach | GROGH | Hüffenhardt | HUEFF | 400 | 2610 | - | 3150 | - | - | 0.518 | 4.7995 | 81.3358 | 18.54
Großgartach-Kupferzell weiss | Großgartach | GROGH | Kupferzell | KUPZL | 400 | 2099 | - | 2280 | - | - | 1.2532 | 13.6558 | 190.1292 | 47.72
Großgartach-Neurott schwarz | Großgartach | GROGH | Neurott | NEURO | 225 | 855 | - | 855 | - | - | 2.3714 | 16.9675 | 249.5995 | 60.82
Großgartach-Pulverdingen rot | Großgartach | GROGH | Pulverdingen | PULVE | 400 | 2507 | - | 2880 | - | - | 0.75677 | 7.8623 | 126.2826 | 29.59
Großgartach-Pulverdingen weiss | Großgartach | GROGH | Pulverdingen | PULVE | 400 | 2500 | - | 2880 | - | - | 0.75662 | 7.8602 | 126.2543 | 29.57
Großkraftwerk Mannheim-Weinheim braun | Großkraftwerk Mannheim | WERKI | Weinheim | WNHEI | 225 | 2505 | - | 2917 | - | - | 0.477 | 3.933 | 77.5659 | 15.96
Grünkraut-Herbertingen rot | Grünkraut | GRKRA | Herbertingen | HRBTG | 400 | 1710 | - | 1710 | - | - | 1.3969 | 12.6489 | 153.3097 | 41.1
Gurtweil-Stockach rot | Gurtweil | GURTW | Stockach | STOCK | 225 | 1980 | - | 1980 | - | - | 2.099 | 16.799 | 348.6225 | 69.8
Heidelberg Süd-Neurott gelb | Heidelberg Süd | HDSUD | Neurott | NEURO | 225 | 542 | - | 542 | - | - | 0.18 | 0.902 | 11.6867 | 3
Heidelberg Süd-Neurott rot | Heidelberg Süd | HDSUD | Neurott | NEURO | 225 | 542 | - | 542 | - | - | 0.18 | 0.902 | 11.6867 | 3
Hoheneck (Amprion)-Herbertingen-Metzingen schwarz HOHCK | Hoheneck (Amprion) | ME_HO | MEZNGY-Y | MEZNGY-Y | 400 | 2552 | - | 3072 | - | - | 1.4957 | 15.7205 | 274.952 | 61.513
Hoheneck (Amprion)-Herbertingen-Metzingen schwarz HRBTG | Metzingen | MEZNGY-Y | Herbertingen (Amprion) | ME_RO | 400 | 2696 | - | 3240 | - | - | 0.0633 | 0.5817 | 10.1159 | 2.27
Hoheneck (Amprion)-Herbertingen-Metzingen schwarz MEZNG | Metzingen | MEZNG | MEZNGY-Y | MEZNGY-Y | 400 | 3000 | - | 3000 | - | - | 0.0481 | 0.7128 | 11.6867 | 2.707
Hoheneck (Amprion)-Pulverdingen weiss | Hoheneck (Amprion) | PU_HO | Pulverdingen | PULVE | 400 | 2880 | - | 2880 | - | - | 0.2672 | 3.4698 | 54.4124 | 12.86
Höpfingen-Grafenrheinfeld gelb | Höpfingen | HOEPF | GR_HO | GR_HO | 400 | 3000 | - | 3000 | - | - | 0.87838 | 10.862 | 193.0666 | 42.25
Höpfingen-Hüffenhardt gelb | Höpfingen | HOEPF | Hüffenhardt | HUEFF | 400 | 2630 | - | 3000 | - | - | 1.3614 | 12.1143 | 204.2664 | 45.38
Hüffenhardt-Neurott-Wiesloch gelb HUEFF | 7590_026-Y | 7590_026-Y | Hüffenhardt | HUEFF | 400 | 2622 | - | 3150 | - | - | 0.9017 | 8.0752 | 144.796 | 31.83
Hüffenhardt-Neurott-Wiesloch gelb NEURO | Neurott | NEURO | 7590_026-Y | 7590_026-Y | 400 | 2622 | - | 3000 | - | - | 0.1968 | 2.0557 | 33.3323 | 7.519
Hüffenhardt-Neurott-Wiesloch gelb WIESL | Wiesloch | WIESL | 7590_026-Y | 7590_026-Y | 400 | 720 | - | 720 | - | - | 0.0608 | 0.5555 | 9.8646 | 2.2
Karlsruhe-Ost-Oberwald rot | Karlsruhe-Ost | KAOST | Oberwald | OWALD | 225 | 720 | - | 720 | - | - | 0.182 | 0.893 | 10.6186 | 2.633
Karlsruhe-West-Daxlanden gelb | Karlsruhe-West | KAWST | Daxlanden | DAXLA | 225 | 769 | - | 769 | - | - | 0.077 | 0.696 | 11.3726 | 2.569
Karlsruhe-West-Daxlanden rot | Karlsruhe-West | KAWST | Daxlanden | DAXLA | 225 | 769 | - | 769 | - | - | 0.077 | 0.696 | 11.3726 | 2.569
Kühmoos-Schwörstadt gelb | Kühmoos | KUHMO | Schwörstadt | SWSDT | 225 | 1237 | - | 1425 | - | - | 0.603 | 2.911 | 34.5575 | 9.6
Kühmoos-Schwörstadt gruen | Kühmoos | KUHMO | Schwörstadt | SWSDT | 225 | 1227 | - | 1425 | - | - | 0.562 | 2.924 | 41.7832 | 9.6
Kupferzell-Stalldorf rot | Kupferzell | KUPZL | Stalldorf | SLDRF | 400 | 3000 | - | 3000 | - | - | 0.9956 | 11.3887 | 217.8693 | 46.79
Marbach-Pulverdingen gruen | Marbach | MARBA | Pulverdingen | PULVE | 225 | 1140 | - | 1140 | - | - | 0.5222 | 4.7578 | 72.8849 | 17.33
Neurott-Philippsburg rot | Neurott | NEURO | Philippsburg | PHILI | 400 | 3000 | - | 3000 | - | - | 0.441 | 6.106 | 94.8447 | 22.1
Neurott-Weinheim rot | Neurott | NEURO | Weinheim | WNHEI | 225 | 2505 | - | 2565 | - | - | 0.792 | 6.545 | 127.8 | 26.45
Neurott-Wiesloch blau | Neurott | NEURO | Wiesloch | WIESL | 225 | 542 | - | 542 | - | - | 0.469 | 2.941 | 35.9712 | 9.6
Oberjettingen-Engstlatt weiss | Oberjettingen | OBJTT | Engstlatt | ENGST | 400 | 2485 | - | 2880 | - | - | 0.8521 | 8.9629 | 144.7332 | 33.82
Oberjettingen-Pulverdingen weiss | Oberjettingen | OBJTT | Pulverdingen | PULVE | 400 | 2486 | - | 2880 | - | - | 1.1665 | 12.1016 | 194.9672 | 45.57
Philippsburg-Pulverdingen weiss | Philippsburg | KKP | Pulverdingen | PULVE | 400 | 2880 | - | 2880 | - | - | 1.3542 | 18.4079 | 284.6597 | 67.68
Pulverdingen-Mühlhausen blau | Pulverdingen | PULVE | Mühlhausen | MULHS | 400 | 2480 | - | 2880 | - | - | 0.7656 | 8.0039 | 134.3973 | 30.7
Stalldorf-Grafenrheinfeld rot | Stalldorf | SLDRF | GR_ST | GR_ST | 400 | 3000 | - | 3150 | - | - | 0.0924 | 1.057 | 19.7606 | 4.293
Wendlingen-Metzingen gelb | Wendlingen | WDLNG | Metzingen | MEZNG | 400 | 2000 | - | 2000 | - | - | 0.4031 | 6.0594 | 96.9495 | 22.682

## Tielines
| Substation 1 |  | Substation 2 |  |  | Maximum Current Imax (A) |  |  | Dynamic line rating (DLR) |  | Electrical Parameters
Circuit name | Full name | Short name | Full name | Short name | Voltage level (kV) | Summer | Interseason | Winter | DLRmin (A) | DLRmax (A) | Resistance R (W) | Reactance X (W) | Susceptance B (mS) | Length TSO Share until border (km)
Asphart (CH)-Sierentz gruen | Asphart (CH) | ASPHA | Sierentz (F) | SIERE | 400 | 1920 | 2300 | 2400 | - | - | 0.739 | 7.1038 | 117.307 | 27.06
Buers (A)-Dellmensingen weiss | Buers (A) | BR_OM | Dellmensingen | DELLM | 400 | 2138 | - | 2138 | - | - | 2.7277 | 22.9215 | 407.0247 | 90.75
Buers (A)-Grünkraut blau | Buers (A) | BR_OM | Grünkraut | GRKRA | 400 | 1800 | - | 1800 | - | - | 0.9131 | 8.775 | 155.5018 | 34.57
Buers (A)-Meiningen (A) | Buers (A) | BR_ME | Meiningen (A) |  | 225 | [9 empty] | Data VUEN
Buers (A)-Walgau (A) | Buers (A) | BR_WA | Walgau (A) |  | 225 | [9 empty] | Data VIW
Buers (A)-Westtirol (A) | Buers (A) | BR_WE | Westtirol (A) |  | 400 | [9 empty] | Data APG
Buers (A)-Westtirol (A) | Buers (A) | BR_WE | Westtirol (A) |  | 225 | [9 empty] | Data APG
Eichstetten-Muhlbach (F) rot | Eichstetten | EICHS | Muhlbach (F) | EI_MU | 400 | 2559 | - | 2850 | - | - | 0.46929 | 4.3766 | 78.2994 | 17.381
Eichstetten-Vogelgrun (F) gelb | Eichstetten | EICHS | Vogelgrun (F) | EI_VO | 225 | 1100 | - | 1302 | - | - | 0.98861 | 5.3927 | 60.9406 | 17.013
Gurtweil-Laufenburg (CH) gelb | Gurtweil | GURTW | Laufenburg (CH) | LA_GU | 225 | 1200 | 1236 | 1547 | - | - | 0.884 | 6.108 | 95.7557 | 21.78
Gurtweil-Oftringen (CH) blau | Gurtweil | GURTW | Oftringen (CH) | GU_OF | 225 | 960 | 1176 | 1265 | - | - | 0.88 | 6.16 | 94.6562 | 22.18
Kühmoos-Asphart (CH) rot | Kühmoos | KUHMO | Asphart (CH) | AS_KU | 400 | 1920 | 2352 | 2530 | - | - | 0.74673 | 6.8225 | 115.1017 | 26.42
Kühmoos-Laufenburg (CH) braun | Kühmoos | KUHMO | Laufenburg (CH) | LA_KU | 400 | 1920 | 2352 | 2400 | - | - | 0.2388 | 2.0353 | 37.7305 | 8.23
Kühmoos-Laufenburg (CH) rot | Kühmoos | KUHMO | Laufenburg (CH) | LA_KU | 400 | 1920 | 2138 | 2138 | - | - | 0.2571 | 2.0979 | 37.4478 | 8.15
Kühmoos-Laufenburg (CH) weiss | Kühmoos | KUHMO | Laufenburg (CH) | LA_KU | 225 | 1130 | 1130 | 1418 | - | - | 0.54 | 2.73 | 31.1018 | 8.58
Kühmoos-Lindenholz (CH) blau | Kühmoos | KUHMO | Lindenholz (CH) | LA_KU | 225 | 900 | 1102 | 1190 | - | - | 0.618 | 3.241 | 37.6991 | 10.24
Laufenburg (CH)-Trossingen rot | Laufenburg (CH) | LA_EN | Trossingen | TRSNG | 400 | 1920 | 2352 | 2400 | - | - | 1.7596 | 21.3243 | 361.1575 | 81.51

## Transformers
Location |  | Voltage Level U (kV) |  | Maximum Current Imax (A) primary |  | Electrical Parameters (primary) |  |  |  | Phase Shifting Properties
Full Name | Short Name | Primary | Secondary | Min | Max | Resistance R (W) | Reactance X (W) | Conductance G (mS) | Susceptance B (mS) | Taps used during FB Qualification | Theta 0 (°) | Symmetrical/Asymmetrical | Phase Regulation du (%) | Angle Regulation du (%)
Daxlanden 401 | DAXLA | 400 | 225 | 1443 | 1443 | 0.24722 | 24.639 | -2.265 | 1.0581 |  | 0 | Symmetrical | 1.389
Neurott 401 | NEURO | 225 | 400 | 1506 | 1506 | 0.19433 | 16.618 | -6.9137 | 4.5558 |  | 0 | Symmetrical | 1.231
Eichstetten | EICHS | 400 | 225 | 1443 | 1443 | 0.24368 | 24.367 | -2.0484 | 1.0731 |  | 0 | Symmetrical | 1.389
Kühmoos | KUHMO | 400 | 225 | 832 | 832 | 0.43636 | 24.554 | -14.7587 | 1.6438 |  | -120 | Asymmetrical |  | 1.385
Neurott 402 | NEURO | 400 | 225 | 953 | 953 | 0.7077 | 24.242 | -3.2286 | 1.47 |  | 0 | Symmetrical | 1.385
Daxlanden 402 | DAXLA | 400 | 225 | 1443 | 1443 | 0.34336 | 24.158 | -7.5816 | 1.6069 |  | 0 | Symmetrical | 1.444
Pulverdingen | PULVE | 225 | 400 | 753 | 753 | 0.54681 | 34.733 | -15.3659 | 3.5274 |  | 90 | Asymmetrical | 1.154 | 1.154
Bürs (A) 31 | BUERS | 225 | 400 | 879 | 879 | 0.3191 | 26.841 | -9.4368 | 2.3535 |  | 0 | Symmetrical | 1.154
Bürs (A) 32 | BUERS | 225 | 400 | 879 | 879 | 0.3174 | 26.902 | -10.8694 | 2.3251 |  | 0 | Symmetrical | 1.154
Bürs (A) 33 | BUERS | 225 | 400 | 879 | 879 | 0.3714 | 26.296 | -6.9725 | 2.3062 |  | 0 | Symmetrical | 1.154
Bürs (A) 37 | BUERS | 225 | 400 | 1106 | 1106 | 0.2149 | 19.315 | -11.2148 | 3.4513 | -10;10 | 90 | Asymmetrical | 1.14 | 1.794
Bürs (A) 34 | BUERS | 225 | 400 | 879 | 879 | 0.3839 | 26.19 | -7.7605 | 1.966 |  | 0 | Symmetrical | 1.154